## Demand Calc
ACWWA Water Demand Estimate and Meter Sizing Using Fixture Values
(Based on AWWA M22 Manual, Second Edition and ACWWA Rules and Regulations)
ACWWA Project Number
Building address or number
Residential or Non-Residential
Pressure Zone at Project
(Obtained from ACWWA or Hydrant Test)
| Fixture Value | Number of | Subtotal
Fixture or Appliance | (at 60 psi) | Fixtures | Fixture Value
Toilet (tank) | 4 |  | 0
Toilet (flush valve) | 35 |  | 0
Urinal (wall or stall) | 16 |  | 0
Urinal (flush valve) | 35 |  | 0
Bidet | 2 |  | 0
Shower (single head) | 2.5 |  | 0
Sink (lavatory) | 1.5 |  | 0
Kitchen Sink | 2.2 |  | 0
Utility Sink | 4 |  | 0 | Pressure Factor (See Pressure Adjustment Factors Tab
Dishwasher | 2 |  | 0 | 20
Bathtub | 8 |  | 0
Clothes Washer | 6 |  | 0
Hose connections (with 50 ft of hose)
1/2 in. | 5 |  | 0 | Residential
5/8 in. | 9 |  | 0 | Non-Residential
3/4 in. | 12 |  | 0
Miscellaneous |  |  |  | 1=Residential, 2=Non-Residential
Bedpan washers | 10 |  | 0 | 1
Drinking fountains | 2 |  | 0
Dental units | 2 |  | 0
Combined Fixture Value |  |  | 0
Residential
Demand (gpm) |  |  | 0 | 0
Non Residential
Pressure Adjustment Factor |  |  | 1.59 | 0
Total Adjusted demand (gpm) |  |  | 0
Required ACWWA Meter Size |  |  | 3/4"

## Residential Curve (hidden)
Residential |  |  | Actual Residential
Ax +Bx^2 + C = y
A | B | C
0.071619 | -2.6972e-05 | 17
x | y |  | x | y |  | Squared Error
18 | 18.2804 |  | 18 | 18 |  | 0.078631
40 | 19.8216 |  | 40 | 20 |  | 0.031818
115 | 24.8795 |  | 115 | 25 |  | 0.014511
205 | 30.5485 |  | 205 | 30 |  | 0.30086
283 | 35.1082 |  | 283 | 35 |  | 0.011703
380 | 40.3207 |  | 380 | 40 |  | 0.10285
460 | 44.2378 |  | 460 | 45 |  | 0.58101
580 | 49.466 |  | 580 | 50 |  | 0.28511
723 | 54.682 |  | 723 | 55 |  | 0.1011
988 | 61.4319 |  | 988 | 60 |  | 2.0503
1250 | 64.3812 |  | 1250 | 65 |  | 0.38288
[5 empty] | Total | 3.9407

## Non-Residential Curve (hidden)
Non-Residential |  |  | Actual Non-Residential
Ax +Bx^2 + C = y
A | B | C
0.11947 | -3.6236e-05 | 38
x | y |  | x | y |  | Squared Error
25 | 40.964 |  | 25 | 40 |  | 0.92936
60 | 45.0376 |  | 60 | 45 |  | 0.0014122
105 | 50.1445 |  | 105 | 50 |  | 0.020894
148 | 54.8874 |  | 148 | 55 |  | 0.012674
190 | 59.3906 |  | 190 | 60 |  | 0.37132
240 | 64.5849 |  | 240 | 65 |  | 0.17229
289 | 69.4995 |  | 289 | 70 |  | 0.25047
338 | 74.2401 |  | 338 | 75 |  | 0.57738
400 | 79.9891 |  | 400 | 80 |  | 0.0001191
452 | 84.596 |  | 452 | 85 |  | 0.16324
518 | 90.161 |  | 518 | 90 |  | 0.025913
578 | 94.9461 |  | 578 | 95 |  | 0.0029033
652 | 100.4885 |  | 652 | 100 |  | 0.23861
723 | 105.4331 |  | 723 | 105 |  | 0.18758
805 | 110.6892 |  | 805 | 110 |  | 0.47496
883 | 115.2366 |  | 883 | 115 |  | 0.05599
978 | 120.1796 |  | 978 | 120 |  | 0.032272
1083 | 124.882 |  | 1083 | 125 |  | 0.013918
1207 | 129.4064 |  | 1207 | 130 |  | 0.35241
[5 empty] | Total | 3.8837

## Pressure Adjustment Factors (hidden)
Pulldown Menu | Working Pressure | Pressure Adjustment
Number | at Meter Discharge | Factor
1 | 35 | 0.74
2 | 40 | 0.8
3 | 45 | 0.85
4 | 50 | 0.9
5 | 55 | 0.95
6 | 60 | 1
7 | 65 | 1.05
8 | 70 | 1.09
9 | 75 | 1.13
10 | 80 | 1.17
11 | 85 | 1.21
12 | 90 | 1.25
13 | 95 | 1.3
14 | 100 | 1.34
15 | 105 | 1.38
16 | 110 | 1.42
17 | 115 | 1.46
18 | 120 | 1.5
19 | 125 | 1.54
20 | 130 | 1.59

## ACWWA Meter Size (hidden)
Design
Meter | Capacity
Size | (gpm)
3/4" | 24
1" | 40
1 1/2" | 80
2" | 128
3" | 250
4" | 400
6" | 800